## Design Conditions
Parameter | Value
Service | Condenser Water
Flow Rate | 3000 GPM
Entering Water Temp | 95°F
Leaving Water Temp | 85°F
Cooling Range | 10°F
Design Wet Bulb | 78°F
Location | Houston, Texas
Elevation | 95 ft

## Selected Equipment
Item | Value
Model | NC8414
Quantity | 2
Configuration | Counterflow
Certification | CTI Certified
Fan Motor | 30 HP
Electrical | 480V / 3PH / 60Hz

## Performance Summary
Requirement | Result
Required Capacity | 1,250 Tons
Selected Capacity | 1,250 Tons
Required Flow | 3,000 GPM
Selected Flow | 3,000 GPM
Required Wet Bulb | 78°F
Supported Wet Bulb | 78°F
CTI Certified | Yes
Meets Duty | Yes

## Sound Analysis
Requirement | Result
Maximum Sound | 75 dBA
Selected Package | Quiet Fan Package
Predicted Sound | 74 dBA
Requirement Met | Yes

## Required Options
Option | Included
VFD Package | Yes
Basin Heater | Yes
Basin Sweeper | Yes
Conductivity Controller | Yes
Vibration Switch | Yes
Access Ladder | Yes
Safety Cage | Yes